## 1. PV power equation

PPV=PSTC⋅GGSTC⋅1γTcTSTC

## 2. Cell temperature model

Cell temperature is not ambient temperature. It is estimated using NOCT model:

Tc=Ta+NOCT-20800⋅G

## 3. Final combined equation

PPV=PSTC⋅G1000⋅1γTa+NOCT-20800G-25

| Symbol | Meaning |  |
| --- | --- | --- |
| Ta | Ambient temperature (°C) |  |
| NOCT | Nominal operating cell temperature (≈ 45°C) |  |
| PPV | Actual PV output power (W) | — |  |
| PSTC | Rated PV power at STC | e.g. 10 kW |  |
| G | Plane-of-array irradiance (W/m²) | 200–1000 |  |
| GSTC | STC irradiance | 1000 W/m² |  |
| Tc | PV cell temperature (°C) | 25–70 |  |
| TSTC | STC temperature | 25 °C |  |
| γ | Power temperature coefficient | −0.003 to −0.005 /°C |  |

At STC:

PSTC=GSTC⋅A⋅ηref
PSTC=1000⋅A⋅ηref

So efficiency and area are absorbed into the rated power.

## 4. Example

10 kW PV system
Irradiance = 800 W/m²
Ambient temperature = 30°C
NOCT = 45°C
γ = −0.004 /°C

### Step 1 – Cell temperature

Tc=30+45-20800⋅800
Tc=30+25=55°C

### Step 2 – Power

PPV=10⋅8001000⋅[1-0.004(55-25)]
PPV=8⋅[1-0.12]=8⋅0.88=7.04 kW